## Sheet1
asset_id | model_name | engine_model | standby_kw | site_type | environment_type | age_years | runtime_hours_since_last_service | pm_interval_hours | air_filter_clean_hours | air_filter_replace_hours | environment_interval_factor | cooling_type | ambient_rating_c | last_service_notes
GEN001 | C70D5 | 4BT3.9 | 70 | small_clinic | standard_indoor | 2 | 180 | 250 | 100 | 500 | 1 | integral_radiator | 40 | No issues found at last visit
GEN002 | C80D5 | 4BT3.9 | 80 | small_clinic | hot_dusty | 4 | 220 | 125 | 50 | 250 | 0.5 | integral_radiator | 50 | Air filter heavily clogged at last visit
GEN003 | DGDK | 6BTA5.9 | 100 | commercial_building | standard_indoor | 3 | 190 | 250 | 100 | 500 | 1 | integral_radiator | 40 | Battery terminals showing minor corrosion
GEN004 | DSGAA | QSB7 | 150 | commercial_building | coastal | 5 | 240 | 125 | 50 | 250 | 0.5 | integral_radiator | 50 | Corrosion noted on external housing last visit
GEN005 | DSGAE | QSB7 | 200 | hospital | standard_indoor | 3 | 200 | 250 | 100 | 500 | 1 | integral_radiator | 40 | All readings normal at last visit
GEN006 | C185D6 | 6CTA8.3 | 170 | hospital | hot_dusty | 6 | 230 | 125 | 50 | 250 | 0.5 | integral_radiator | 50 | Coolant level low at last visit topped up
GEN007 | DGFA | 6CTA8.3 | 160 | data_center | standard_indoor | 2 | 150 | 250 | 100 | 500 | 1 | integral_radiator | 40 | New unit no issues found
GEN008 | DGFC | 6CTAA8.3 | 200 | data_center | hot_dusty | 7 | 260 | 125 | 50 | 250 | 0.5 | integral_radiator | 50 | Belt showing wear flagged for monitoring
GEN009 | C275D2RE | QSL9 | 275 | data_center | standard_indoor | 4 | 210 | 250 | 100 | 500 | 1 | remote_radiator | 40 | Minor fuel leak repaired at last visit
GEN010 | C300D6R | QSM11 | 300 | data_center | hot_dusty | 5 | 245 | 125 | 50 | 250 | 0.5 | remote_radiator | 50 | Air filter replaced cooling system flushed
GEN011 | DFCC | NTA855 | 350 | hospital | coastal | 6 | 235 | 125 | 50 | 250 | 0.5 | remote_radiator | 50 | Corrosion on battery terminals treated
GEN012 | DFEK | QSX15 | 500 | data_center | standard_indoor | 3 | 180 | 250 | 100 | 500 | 1 | remote_radiator | 40 | All systems normal at last visit
GEN013 | DFEJ | QSX15 | 450 | hospital | hot_dusty | 8 | 270 | 125 | 50 | 250 | 0.5 | remote_radiator | 50 | Aging battery borderline voltage reading flagged
GEN014 | DQPAA | QSK19 | 600 | data_center | standard_indoor | 4 | 200 | 250 | 100 | 500 | 1 | remote_radiator | 40 | Coolant flush completed all normal
GEN015 | DQPAB | QSK19 | 700 | data_center | coastal | 5 | 225 | 125 | 50 | 250 | 0.5 | remote_radiator | 50 | Salt corrosion on external components noted
GEN016 | DQCA | QSK23 | 750 | hospital | standard_indoor | 6 | 215 | 250 | 100 | 500 | 1 | remote_radiator | 40 | Thermostat replaced runs stable
GEN017 | DQCC | QSK23 | 800 | data_center | hot_dusty | 9 | 280 | 125 | 50 | 250 | 0.5 | remote_radiator | 55 | Multiple borderline readings needs attention
GEN018 | DQGAE | QSK50 | 1250 | data_center | standard_indoor | 5 | 195 | 250 | 100 | 500 | 1 | remote_radiator | 40 | Major overhaul completed 6 months ago
GEN019 | DQGAR | QSK50 | 1400 | hospital | hot_dusty | 10 | 290 | 125 | 50 | 250 | 0.5 | remote_radiator | 40 | Oldest unit multiple worn components flagged
GEN020 | DFLE | KTA50 | 1500 | data_center | standard_indoor | 3 | 170 | 250 | 100 | 500 | 1 | remote_radiator | 40 | Recently commissioned running well